{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Статистика "],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Статистика ","index":0,"n_rows":163,"n_cols":12,"rows_kept":163,"cut":false,"hidden":false,"merged":[[47,2,56,2],[47,7,56,7],[47,8,56,8],[67,2,71,2],[67,0,71,0],[47,0,56,0],[67,7,71,7],[67,8,71,8],[96,0,97,0],[96,8,97,8],[96,7,97,7],[74,2,77,2],[74,0,77,0],[1,0,1,8],[21,2,26,2],[21,8,26,8],[21,0,26,0],[34,0,41,0],[34,2,41,2],[34,7,41,7],[34,8,41,8],[21,7,26,7],[78,0,81,0],[74,7,77,7],[74,8,77,8],[78,8,81,8],[78,7,81,7],[78,2,81,2]]}
[]
["                    Статистика актов расследования причин аварии 2017г."]
[]
["Кол-во отказавшего оборудования","Дата","Место","Время начала (часы, мин., год, день, мес.)","Время устранения аварийного режима (часы, мин., год, день, мес.)","Время простоя (час)","Недоотпуск эл. энергии (тыс. кВт*час)","Причина возникновения","№   акта расследования причин аварии"]
[1,"2017-01-05","КЛ-10кВ РП-3 яч.10 - ТП-371 яч.2","2017-01-05T22:50:00","2017-01-05T23:18:00",0.46666666661622003,3.8126666662545175E-2,"МУП \"Электросеть\" , соед. муфта, 1959г.","№01 от 19.01.2017"]
[2,"2017-01-08","КЛ-10кВ ТП-2015 яч.3 - ТП-70 яч.3","2017-01-08T21:38:00","2017-01-08T22:38:00",1.0000000001164153,0.32800000003818425,"МУП \"Электросеть\" , соед. муфта,2006г.","№02 от 25.01.2017"]
[3,"2017-01-10","ГПП-9- трансформатор ЭВ-2 110кВ","2017-01-10T09:58:00","2017-01-10T09:58:00",0,0,"МУП \"Электросеть\" , проходной изолятор (попадание птицы)","№03 от 18.01.2017"]
[4,"2017-01-10","КЛ-10кВ ГПП-\"Заягорба\" яч.103 - РП-7 яч.3","2017-01-10T12:14:00","2017-01-10T12:14:00",0,0,"МУП \"Электросеть\",  соед. муфта, 1988г.","№04 от 26.01.2017"]
[5,"2017-01-14","КЛ-10кВ ГПП-\"Первомайская\" яч.303 - РП-10 яч.8","2017-01-14T14:44:00","2017-01-14T14:44:00",0,0,"МУП \"Электросеть\",целое место, 1989г.","№05 от 31.01.2017"]
[6,"2017-01-14","КЛ-10кВ РП-15 яч.12 - ТП-235 яч.2","2017-01-14T14:44:00","2017-01-14T15:40:00",0.93333333340706304,0.29026666668959661,"МУП \"Электросеть\",целое место, 1980г.","№06 от 31.01.2017"]
[7,"2017-01-24","КЛ-10кВ РП-27 яч.24 - ТП-1064 яч.3","2017-01-24T10:22:00","2017-01-24T13:15:00",2.8833333334769122,0.84712333337551682,"ООО \"ПСМО-98\", соед. муфта, 2014г. ","№07 от 06.02.2017"]
[8,"2017-02-01","II СШ РУ-10кВ РП-15","2017-02-01T16:24:00","2017-02-01T17:17:00",0.88333333324408159,2.8001666663837388,"откл. ВВ яч.8 РУ-10кВ РП-15 \", \"ФСК ЕЭС\", МУП \"Электросеть\" (дефект конструкции оборудования яч.302 ПС 220/10 \"Первомайская\", неселективеная работа РЗиА яч.4 РП-15)","№09 от 20.02.2017"]
[9,"2017-02-04","КЛ-10кВ ТП-2010 яч.7 - ТП-2013 яч.2; КЛ-10кВ ТП-2013 яч.5 - ТП-4 яч.3","2017-02-04T14:20:00","2017-02-04T17:45:00",3.4166666668024845,1.0352500000411529,"ООО ПКФ \"Антей\" повреждена изоляция КЛ-10кВ методом \"ГНБ\"вследствии отклонения от проектоной схемы","№10 от 13.02.2017"]
[10,"2017-02-03","КЛ-10кВ ГПП-9 яч.107 - РП-17 яч.8 (каб. \"А\")","2017-02-03T01:05:00","2017-02-03T01:05:00",0,0,"МУП \"Электросеть\",целое место, 1980г.","№11 от 22.02.2017"]
[11,"2017-02-04","КЛ-10кВ ТП-2015 яч.5 - ТП-2017 яч.5","2017-02-04T14:20:00","2017-02-04T15:33:00",1.216666666790843,0.35405000003613529,"МУП \"Электросеть\",соед. муфта , 1989г.","№12 от 14.02.2017"]
[12,"2017-02-07","КЛ-10кВ РП-25 яч.12 - РП-13 яч.10 (перемычка)","2017-02-07T06:27:00","2017-02-07T06:27:00",0,0,"ООО \"ПСМО-98\",соед. муфта , 2013г.","№13 от 22.02.2017"]
[13,"2017-02-07","КЛ-10кВ ТП-392 яч.1 - ТП-334 яч.2; КЛ-10кВ ТП-346 яч.4 - ТП-392 яч.5","2017-02-07T15:51:00","2017-02-07T19:09:00",3.3000000001047738,2.4416238000775206,"МУП \"Электросеть\" целое место , 1967г., конц. разд., 1968г.","№14 от 14.02.2017"]
[14,"2017-02-07","КЛ-10кВ РП-4 яч.3 - ТП-340 яч.1","2017-02-07T15:51:00","2017-02-07T19:09:00",3.3000000001047738,1.7746971000563461,"МУП \"Электросеть\" целое место , 1972г.","№15 от 15.02.2017"]
[15,"2017-02-09","КЛ-10кВ ГПП-\"Заягорба\" яч.306 - РП-15 яч.3","2017-02-09T02:48:00","2017-02-09T02:48:00",0,0,"МУП \"Электросеть\" целое место , 1980г.","№16 от 16.02.2017"]
[16,"2017-02-12","КЛ-10кВ ТП-384 яч.2 - ТП-387 яч.3","2017-02-12T13:05:00","2017-02-12T13:05:00",0,0,"МУП \"Электросеть\" целое место , 1964г.","№17 от 27.02.2017"]
[17,"2017-02-22","КЛ-10кВ РП-9 яч.14 - ТП-86 яч.1, КЛ-10кВ ТП-86 яч.3 - ТП-107 яч.1","2017-02-22T20:15:00","2017-02-23T01:30:00",5.25,1.1868989999999999,"МУП \"Электросеть\" целое место , 1979г., соед. муфта., 1977г.","№18 от 09.03.2017"]
[18,"2017-03-05","КЛ-10кВ РП-12 яч.12 - ТП-172 яч.1А","2017-03-05T07:04:00","2017-03-05T08:05:00",1.0166666666627862,9.9633333332953045E-2,"ООО \"ПСМО-98\",соед. муфта , 2010г.","№19 от 22.03.2017"]
[null,"2017-03-05",null,"2017-03-05T07:04:00","2017-03-05T08:05:00",1.0166666666627862,7.9299999999697321E-2,0]
[null,"2017-03-05",null,"2017-03-05T07:04:00","2017-03-05T08:05:00",1.0166666666627862,6.9133333333069452E-2,0]
[null,"2017-03-05",null,"2017-03-05T07:04:00","2017-03-05T08:20:00",1.2666666666045785,0.11526666666101665,"ООО \"ПСМО-98\",соед. муфта , 2010г."]
[null,"2017-03-05",null,"2017-03-05T07:04:00","2017-03-05T08:40:00",1.5999999999767169,2.5599999999627469E-2,0]
[null,"2017-03-05",null,"2017-03-05T07:04:00","2017-03-05T08:40:00",1.5999999999767169,9.5999999998603022E-2,0]
[19,"2017-03-11","ГПП \"Зашекснинская\" яч.13-РП-22 яч.6 (каб. \"А\", \"В\")","2017-03-11T08:45:00","2017-03-11T09:34:00",0.8166666665347293,1.0257333331676199,"МУП \"Электросеть\" целое место , 1979г., соед. муфта, 1977г.  ","№20 от 22.03.2017"]
[20,"2017-03-19","КЛ-10кВ ТП-61 яч.2 - ТП-2 яч.4 (каб. \"В\")","2017-03-19T11:32:00","2017-03-19T12:36:00",1.0666666666511446,0.38547093332772403,"МУП \"Электросеть\" соед. муфта , 1951г.","№21 от 31.03.2017"]
[21,"2017-03-20","КЛ-10кВ ТП-2017 яч.2 - ТП-53 яч.1","2017-03-20T09:42:00","2017-03-20T10:29:00",0.78333333326736465,0.24685653331254426,"ООО \"Жилстройзаказчик\" ковшом экскаватора повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место, 1961г.)","№22 от 21.03.2017"]
[22,"2017-03-25","КЛ-10кВ ГПП-\"Заягорба\" яч.414 - РП-8 яч.8 (каб. \"В\")","2017-03-25T19:21:00","2017-03-25T19:21:00",0,0,"МУП \"Электросеть\"  целое место , 1983г.","№23 от 11.04.2017"]
[23,"2017-03-25","КЛ-10кВ ТП-355 яч.1 - ТП-364 яч.3","2017-03-25T22:47:00","2017-03-25T23:58:00",1.1833333333488554,0.54802533334052195,"МУП \"Электросеть\"  целое место , 1983г.","№24 от 11.04.2017"]
[24,"2017-04-13","КЛ-10кВ ТП-1811 яч.6 - ТП-1810 яч.5","2017-04-13T11:28:00","2017-04-13T12:14:00",0.76666666672099382,6.9234600004906069E-2,"частное лицо Долмазов Л.С. ковшом экскаватора повреждена изоляция КЛ-10кВ . Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место. 1982г.)","№25 от 17.04.2017"]
[25,"2017-04-18","КЛ-10кВ ТП-1811 яч.6 - ТП-1810 яч.5","2017-04-18T07:28:00","2017-04-18T08:12:00",0.73333333327900618,3.197039999763155E-2,"неустановленные лица (целое место, 1982г.)","№26 от 20.04.2017"]
[26,"2017-04-18","КЛ-10кВ ТП-111 яч.2 - ТП-82 яч.2, ТП-111 яч.3- ТП-138 яч.1","2017-04-18T10:00:00","2017-04-18T10:38:00",0.63333333347691223,9.3100000021106091E-2,"ООО \"ПМК-2\" ковшом экскаватора повреждена изоляция КЛ-10кВ . Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место, 1978г., целое место, 1978г.)","№27 от 24.04.2017"]
[null,"2017-04-18",null,"2017-04-18T10:00:00","2017-04-18T10:38:00",0.63333333347691223,0]
[null,"2017-04-18",null,"2017-04-18T10:00:00","2017-04-18T11:38:00",1.6333333334187046,0]
[null,"2017-04-18",null,"2017-04-18T10:00:00","2017-04-18T11:44:00",1.7333333333954215,0]
[null,"2017-04-18",null,"2017-04-18T10:00:00","2017-04-18T11:44:00",1.7333333333954215,2.7733333334326746E-2]
[null,"2017-04-18",null,"2017-04-18T10:00:00","2017-04-18T11:52:00",1.8666666666395031,1.8666666666395031E-2]
[null,"2017-04-18",null,"2017-04-18T10:00:00","2017-04-18T11:52:00",1.8666666666395031,0.33599999999511054]
[null,"2017-04-18",null,"2017-04-18T10:00:00","2017-04-18T15:23:00",5.3833333334187046,9.6900000001536687E-2]
[27,"2017-04-18","КЛ-10кВ ТП-1811 яч.1 - ТП-189 яч.1","2017-04-18T16:02:00","2017-04-18T17:58:00",1.9333333333488554,9.632640000077336E-2,"частное лицо Долмазов Л.С. ковшом экскаватора повреждена изоляция КЛ-10кВ . Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место, 1983г.)","№28 от 25.04.2017"]
[28,"2017-04-21","КЛ-10кВ ТП-14 яч.3 - ТП-34 яч.1","2017-04-21T09:28:00","2017-04-21T09:55:00",0.45000000006984919,0.20949435003251782,"ООО \"Череповецсетьстрой\" перфотатором повреждена изоляция КЛ-10кВ . Не выполнено укрепление вскрытой КЛ-10кВ для защиты от мех. повреждений ( целое место, 1959г.)","№29 от 27.04.2017"]
[29,"2017-04-24","КЛ-10кВ ТП-256 яч.3 - ТП-258 яч.6","2017-04-24T05:06:00","2017-04-24T06:00:00",0.8999999999650754,0.25223399999021201,"МУП \"Электросеть\" соед. муфта , 1985г.","№30 от 28.04.2017"]
[30,"2017-04-26","КЛ-10кВ ГПП-Зашекснинская яч.35 - КТПН-ПК (ф. \"ЗОС-2\")","2017-04-26T16:54:00","2017-04-26T16:54:00",0,0,"МУП \"Электросеть\" соед. муфта , 1985г.","№31 от 02.05.2017"]
[31,"2017-04-26","КЛ-10кВ ТП-805 яч.4 - ТП-811 яч.1","2017-04-26T22:07:00","2017-04-26T23:17:00",1.1666666666278616,0.44322833331859091,"МУП \"Электросеть\" целое место , 1963г.","№32 от 10.05.2017"]
[32,"2017-04-26","КЛ-10кВ ТП-97 яч.2 - ТП-110 яч.3","2017-04-26T22:07:00","2017-04-27T00:27:00",2.3333333334303461,0.13766666667239041,"МУП \"Электросеть\" соед. муфта , 1985г.","№33 от 10.05.2017"]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-27T00:30:00",2.3833333334187046,0.15730000000563449]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-27T00:30:00",2.3833333334187046,0.11678333333751652]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-27T00:47:00",2.6666666666278616,3.4666666666162201E-2]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-27T00:47:00",2.6666666666278616,0.37866666666115634]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-27T00:30:00",2.3833333334187046,0.2693166666763136]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-27T00:30:00",2.3833333334187046,0.46236666668322868]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-26T23:50:00",1.7166666666744277,0.21286666666762905]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-26T23:44:00",1.6166666666977108,0.12771666666911916]
[null,"2017-04-26",null,"2017-04-26T22:07:00","2017-04-27T00:15:00",2.1333333333022892,0.11519999999832362]
[33,"2017-04-29","КЛ-10кВ ТП-194 яч.2 - ТП-196 яч.4","2017-04-29T00:29:00","2017-04-29T01:10:00",0.68333333329064772,0.14043866665789392,"МУП \"Электросеть\" каб.разд. , 1972г.","№34 от 02.05.2017"]
[34,"2017-05-01","КЛ-10кВ РП-12 яч.19 - ТП-1812 яч.4","2017-05-01T23:25:00","2017-05-02T00:29:00",1.0666666666511446,0.44841599999347465,"МУП \"Электросеть\" соед. муфта , 1985г.","№35 от 15.05.2017"]
[35,"2017-05-09","КЛ-10кВ ГПП-Искра яч.305 - РП-14 яч.12","2017-05-09T18:19:00","2017-05-09T18:19:00",0,0,"ООО \"ПСМО-98\",соед. муфта , 2014г.","№36 от 22.05.2017"]
[36,"2017-05-11","КЛ-10кВ РП-12 яч.9 - ТП-251 яч.2","2017-05-11T14:57:00","2017-05-11T14:57:00",0,0,"МУП \"Электросеть\" целое место , 1976г.","№37 от 15.05.2017"]
[37,"2017-05-12","КЛ-10кВ ТП-123 яч.3 - 2ПАП яч.2","2017-05-12T12:06:00","2017-05-12T12:59:00",0.88333333341870457,0.33833433336603219,"МУП \"Электросеть\" соед. муфта , 1985г.","№38 от 22.05.2017"]
[38,"2017-05-12","КЛ-10кВ ГПП-Заягорба яч.412 РП- 20 яч.8","2017-05-12T12:52:00","2017-05-12T12:52:00",0,0,"МУП \"Электросеть\" соед. муфта , 1985г.","№39 от 22.05.2017"]
[39,"2017-05-14","КЛ-10кВ РПП-1 яч.104 - РП-9 яч.7","2017-05-14T10:09:00","2017-05-14T10:38:00",0.48333333333721384,0.90757433334061988,"брак ПСМО (целое место, 2015г.)","№40 от 17.05.2017"]
[40,"2017-05-16","КЛ-10кВ ТП-32  - ТП-31 яч.6","2017-05-16T10:13:00","2017-05-16T11:15:00",1.03333333338378,8.3658666670750823E-2,"МУП \"Водоканал\" ковшом экскаватора повреждена изоляция КЛ-10кВ . Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место, 1960г.)","№41 от 19.05.2017"]
[41,"2017-05-16","КЛ-10кВ РП-22 яч.18 - КНС №6 ввод №2","2017-05-16T14:30:00","2017-05-16T14:30:00",0,0,"ООО \"Спецэлектромонтаж\"  ковшом экскаватора повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место, 1987г.)","№42 от 19.05.2017"]
[42,"2017-05-18","КЛ-10кВ РП-24 яч.5 -ТП-2113 яч.3 ","2017-05-18T01:28:00","2017-05-18T01:47:00",0.31666666665114462,2.563733333207667E-2,"МУП \"Электросеть\" соед. муфта , 1994г.","№43 от 01.06.2017"]
[43,"2017-05-26","КЛ-10кВ РП-4 яч.3 -ТП-340 яч.1 , ТП-340 яч.2-ТП-343 яч.4","2017-05-26T07:45:00","2017-05-26T08:10:00",0.41666666680248454,5.1833333350229084E-2,"МУП \"Электросеть\" целое место , 1976г.","№44 от 05.06.2017"]
[null,"2017-05-26",null,"2017-05-26T07:45:00","2017-05-26T08:20:00",0.58333333331393078,4.0599999998649581E-3]
[null,"2017-05-26",null,"2017-05-26T07:45:00","2017-05-26T08:40:00",0.91666666668606922,3.4650000000733414E-2]
[null,"2017-05-26",null,"2017-05-26T07:45:00","2017-05-26T08:50:00",1.0833333333721384,3.1200000001117586E-3]
[null,"2017-05-26",null,"2017-05-26T07:45:00","2017-05-26T11:20:00",3.5833333333139308,0.30959999999832366]
[44,"2017-05-31","КЛ-10кВ ТП-18 яч.3 -ТП-841 яч.1","2017-05-31T09:40:00","2017-05-31T10:52:00",1.1999999998952262,0.25223399997797707,"МУП \"Электросеть\" целое место , 1962г.","№45 от 07.05.2017"]
[45,"2017-06-01","КЛ-10кВ РП-15 яч.2 -ПНС-11 яч.2","2017-06-01T02:55:00","2017-06-01T05:45:00",2.8333333333139308,7.0549999999516874E-2,"МУП \"Электросеть\" каб.разд. , 1988г.","№46 от 06.05.2017"]
[46,"2017-06-01","КЛ-10кВ ТП-230 яч.5 -ТП-238 яч.2","2017-06-01T03:26:00","2017-06-01T04:37:00",1.1833333333488554,6.3900000000838189E-2,"МУП \"Электросеть\" соед. муфта , 1979г.","№47 от 07.06.2017"]
[null,"2017-06-01",null,"2017-06-01T03:26:00","2017-06-01T04:46:00",1.3333333333139308,0.10133333333185873]
[null,"2017-06-01",null,"2017-06-01T03:26:00","2017-06-01T05:09:00",1.7166666666744277,6.6950000000302684E-2]
[null,"2017-06-01",null,"2017-06-01T03:26:00","2017-06-01T05:23:00",1.9500000000698492,0.10530000000377186]
[47,"2017-06-01","КЛ-10кВ РП-15 яч.10 -ТП-236 яч.1","2017-06-01T02:52:00","2017-06-01T08:37:00",5.7500000000582077,0.73117000000740162,"МУП \"Электросеть\" соед. муфта , 1980г.","№48 от 06.06.2017"]
[null,"2017-06-01",null,"2017-06-01T02:52:00","2017-06-01T09:11:00",6.3166666668257676,7.5800000001909215E-2]
[null,"2017-06-01",null,"2017-06-01T02:52:00","2017-06-01T04:12:00",1.3333333334885538,4.8000000005587934E-2]
[null,"2017-06-01",null,"2017-06-01T02:52:00","2017-06-01T04:12:00",1.3333333334885538,2.4000000002793967E-2]
[48,"2017-06-01","КЛ-10кВ ГПП \"Первомайская\" яч.303 - РП-10 яч.8 ф. \"ЖР-11\"","2017-06-01T03:43:00","2017-06-01T03:43:00",0,0,"МУП \"Электросеть\" целое место , 1962г.","№49 от 08.06.2017"]
[49,"2017-06-02","КЛ-10кВ ТП-300 яч.2 -ТП-301 яч.1","2017-06-02T02:06:00","2017-06-02T02:40:00",0.56666666659293696,9.7013333320710798E-2,"МУП \"Электросеть\" целое место , 1961г.","№50 от 08.06.2017"]
[50,"2017-06-09","КЛ-10кВ ТП-45 яч.1 -ТП-46 яч.1","2017-06-09T15:55:00","2017-06-09T16:15:00",0.33333333337213844,1.3649666668255695E-2,"МУП \"Электросеть\"  соед. муфта , 1984г.","№51 от 27.06.2017"]
[51,"2017-06-09","КЛ-10кВ РП-11 яч.4 -ТП-1000 яч.4","2017-06-09T15:55:00","2017-06-09T17:00:00",1.0833333333721384,2.3614500000845872E-2,"ООО СК \"Стройновация\" при проезде крупногабаритной техникой повреждена изоляция КЛ-10кВ, при закопке траншеи КЛ-10кВ не выполнена подсыпка из песка (песчаная подушка) ( соед. муфта, 1986г.)","№52 от 27.06.2017"]
[52,"2017-06-19","КЛ-10кВ РП-25 яч.14 -ТП-149 яч.1 (каб. \"А\")","2017-06-19T18:52:00","2017-06-19T19:30:00",0.63333333330228925,7.6915799996229828E-2,"МУП \"Электросеть\" целое место , 1992г.","№53 от 05.07.2017"]
[53,"2017-06-21","КЛ-10кВ РП-4 яч.3 -ТП-340 яч.1 ","2017-06-21T01:55:00","2017-06-21T02:55:00",1.0000000001164153,0.22265100002591998,"МУП \"Электросеть\" целое место , 1972г.","№54 от 03.07.2017"]
[54,"2017-06-24","КЛ-10кВ РП-10 яч.11 -ТП-109 яч.1 ","2017-06-24T20:27:00","2017-06-24T21:30:00",1.0500000001047738,8.9916750008972313E-2,"МУП \"Электросеть\" целое место , 1976г.","№55 от 06.07.2017"]
[55,"2017-06-26","КЛ-10кВ РП-6 яч.15 -ТП-143 яч.2 ","2017-06-26T10:51:00","2017-06-26T11:08:00",0.28333333338377997,4.2350400007540367E-2,"МУП \"Электросеть\" каб.разд. , 1969г.","№56 от 04.07.2017"]
[56,"2017-06-27","КЛ-10кВ РП-4 яч.4 -ТП-389 яч.2 ","2017-06-27T09:44:00","2017-06-27T10:38:00",0.90000000013969839,0.28166130004371959,"АО \"Газпромгазораспределение Вологда\"  ковшом экскаватора повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место, 1964г.)","№57 от 03.07.2017"]
[57,"2017-06-30","КЛ-10кВ РП-11 яч.2 -ТП-5 яч.1","2017-06-30T12:54:00","2017-06-30T14:10:00",1.2666666667792015,0.19327560001717126,"МУП \"Электросеть\"  соед. муфта , 1995г.","№58 от 12.07.2017"]
[58,"2017-07-06","КЛ-10кВ ГПП-Заш. яч.35 - ТП-ПК  ф. ЗОС-2","2017-07-06T15:28:00","2017-07-06T15:28:00",0,0,"МУП \"Электросеть\" целое место , 1985г.","№59 от 17.07.2017"]
[59,"2017-07-07","КЛ-10кВ РП-19 яч.17 - ТП-144  яч.1","2017-07-07T11:19:00","2017-07-07T11:19:00",0,0,"МУП \"Электросеть\" целое место , 1987г.","№60 от 17.07.2017"]
[60,"2017-07-15","КЛ-10кВ РП-15 яч.12 - ТП-235  яч.2","2017-07-15T16:33:00","2017-07-15T17:03:00",0.50000000005820766,0.14013000001631326,"МУП \"Электросеть\" целое место , 1980г.","№61 от 20.07.2017"]
[61,"2017-07-15","КЛ-10кВ ГПП-Заягорба яч.414 - РП-8  яч.8 (В)","2017-07-15T21:47:00","2017-07-15T21:47:00",0,0,"Брак \"ПСМО\" (целое место, 2012г.)","№62 от 24.07.2017"]
[62,"2017-07-19","КЛ-10кВ ГПП-4  яч.33 - РП-1 яч.13 ","2017-07-19T14:13:00","2017-07-19T14:20:00",0.11666666652308777,0.3207936662718735,"МУП \"Электросеть\" соед. муфта , 1959г., целое место, 1951г.","№63 от 31.07.2017"]
[null,"2017-07-19","КЛ-10кВ РП-1 яч.17 - ТП-364  яч.1","2017-07-19T14:22:00","2017-07-19T15:10:00",0.79999999998835847,0.71584559998958308]
[63,"2017-07-24","КЛ-10кВ РП-1 яч.3 - ТП-18  яч.4","2017-07-24T11:44:00","2017-07-24T13:20:00",1.5999999999767169,0.52564319999235087,"МУП \"Электросеть\" целое место , 1962г.","№64 от 01.08.2017"]
[64,"2017-07-24","КЛ-10кВ ГПП-9 яч.408 - РП-17  яч.7 (каб. \"В\")","2017-07-24T11:57:00","2017-07-24T11:57:00",0,0,"ООО \"Техстрой\"   ковшом экскаватора повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление (целое место, 2008г.)","№65 от 31.07.2017"]
[65,"2017-07-24","КЛ-10кВ ГПП-9 яч.203 - РП-2  яч.15 (каб. \"В\")","2017-07-24T12:46:00","2017-07-24T12:46:00",0,0,"ПАО \"Северсталь\"  ковшом экскаватора повреждена изоляция КЛ-10кВ, вследствии отклонения от проектоной схемы (целое место, 2007г.)","№67 от 26.07.2017"]
[66,"2017-07-29","КЛ-10кВ РП-3 яч.21 - ТП-395  яч.2","2017-07-29T13:27:00","2017-07-29T14:12:00",0.75,2.3355000000000001E-2,"МУП \"Электросеть\" каб.разд. , 1967г.","№66 от 02.08.2017"]
[67,"2017-07-29","КЛ-10кВ РП-14 яч.18 - ТП-910  яч.6","2017-07-29T07:32:00","2017-07-29T08:10:00",0.63333333347691223,9.8610000022355242E-3,"МУП \"Электросеть\" целое место. , 1989г.","№68 от 14.08.2017"]
[68,"2017-07-29","КЛ-10кВ ТП-21 яч.3 - ТП-58А  яч.2","2017-07-29T07:31:00","2017-07-29T09:15:00",1.7333333332207985,7.286759999526915E-2,"МУП \"Электросеть\" каб.разд. , 1988г.","№69 от 04.08.2017"]
[69,"2017-07-29","КЛ-10кВ ТП-62 яч.1 - ТП-97  яч.5","2017-07-29T07:34:00","2017-07-29T09:00:00",1.4333333332906477,0.40616939998790408,"МУП \"Электросеть\" каб.разд. , 1973г.","№70 от 04.08.2017"]
[70,"2017-07-29","КЛ-10кВ ГПП-Искра яч.309 - РП-19  яч.7 ","2017-07-29T07:40:00","2017-07-29T07:40:00",0,0,"Брак ПСМО","№71 от 10.08.2017"]
[71,"2017-08-01","КЛ-10кВ ТП-3 яч.4 - ТП-11  яч.4","2017-08-01T11:09:00","2017-08-01T12:05:00",0.93333333323244005,0.26666266663784038,"МУП \"Электросеть\" целое место. , 1962г.","№72 от 08.08.2017"]
[72,"2017-08-01","КЛ-10кВ ГПП-Искра яч.305 - РП-14  яч.12 (В)","2017-08-01T11:09:00","2017-08-01T11:24:00",0.24999999994179234,0.47410649988961345,"Брак ПСМО","№73 от 09.08.2017"]
[73,"2017-08-03","КЛ-10кВ ТП-2113 яч.6 - ТП-2114  яч.3","2017-08-03T02:01:00","2017-08-03T02:50:00",0.81666666670935228,0.22633590001183015,"МУП \"Электросеть\" целое место. , 1995г.","№74 от 21.08.2017"]
[74,"2017-08-02","КЛ-10кВ ТП-336 яч.2 - ТП-392  яч.3","2017-08-02T15:06:00","2017-08-02T15:30:00",0.40000000008149073,0.18497160003768365,"ООО \"Вектор\" повреждена изоляция КЛ-10кВ методом \"ГНБ\" вследствии отклонения от проектоной схемы","№75 от 07.08.2017"]
[75,"2017-08-03","КЛ-10кВ ТП-229 яч.2 - ТП-223  яч.2","2017-08-03T02:46:00","2017-08-03T03:20:00",0.56666666676755995,0.11469900002042181,"МУП \"Электросеть\" целое место. , 1973г.","№76 от 04.08.2017"]
[76,"2017-08-04","КЛ-10кВ ГПП-9 яч.408 - РП-17  яч.7 (А)","2017-08-04T10:40:00","2017-08-04T10:40:00",0,0,"ООО \"Техстрой\"   ковшом экскаватора повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление","№77 от 11.08.2017"]
[77,"2017-08-09","КЛ-10кВ РП-17 яч.11 - РП-22  яч.3 (А)","2017-08-09T07:17:00","2017-08-09T07:17:00",0,0,"ООО ПКФ \"Антей\"   ковшом экскаватора повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление","№78 от 14.08.2017"]
[78,"2017-08-11","КЛ-10кВ ТП-41 яч.3 - ТП-159  яч.1","2017-08-11T10:32:00","2017-08-11T13:49:00",3.28333333338378,3.803413333391771,"МУП \"Электросеть\" соед.муфта. , 1972г.","№79 от 15.08.2017"]
[79,"2017-08-11","КЛ-10кВ ТП-63 яч.1 - ТП-57  яч.2","2017-08-11T11:16:00","2017-08-11T13:29:00",2.2166666665580124,0.39345389998071406,"МУП \"Электросеть\" соед.муфта. , 1963г.","№80 от 18.08.2017"]
[80,"2017-08-11","КЛ-10кВ ТП-107 яч.11 - ТП-86  яч.3","2017-08-11T10:32:00","2017-08-11T14:03:00",3.5166666667792015,0.64062765002050037,"МУП \"Электросеть\" целое место. , 1976г.","№81 от 30.08.2017"]
[81,"2017-08-11","КЛ-10кВ ГПП-Первомайская яч.102 - РП-24  яч.3","2017-08-11T21:49:00","2017-08-11T21:49:00",0,0,"МУП \"Электросеть\" целое место. , 1991г.","№82 от 21.08.2017"]
[82,"2017-08-11","КЛ-10кВ ГПП-Первомайская яч.105 - РП-28  яч.4","2017-08-11T17:11:00","2017-08-11T17:11:00",0,0,"МУП \"Электросеть\" целое место. , 1998г.","№83 от 15.08.2017"]
[83,"2017-08-13","КЛ-10кВ ГПП-9 яч.107 - РП-17  яч.8 (каб. \"А\")","2017-08-13T17:49:00","2017-08-13T17:49:00",0,0,"МУП \"Электросеть\" соед.муфта. , 1990г.","№84 от 21.08.2017"]
[84,"2017-08-14","КЛ-10кВ ГПП-Первомайская яч.103 - РП-11  яч.3 (каб. \"А\")","2017-08-14T19:35:00","2017-08-14T19:35:00",7.7609918491816643E-11,0,"МУП \"Электросеть\" соед.муфта. , 1974г.","№86 от 24.08.2017"]
[85,"2017-08-14","КЛ-10кВ РП-15 яч.9 - ТП-174  яч.1А","2017-08-14T16:01:00","2017-08-14T16:50:00",0.81666666670935228,0.13040533334014939,"МУП \"Электросеть\" целое место. , 1979г.","№85 от 31.08.2017"]
[86,"2017-08-15","КЛ-10кВ ГПП-Зашекснинская яч.24 - РП-26  яч.11 (каб. \"А\", \"В\")                       ","2017-08-15T05:53:00","2017-08-15T05:53:00",3.1043834169963702E-11,0,"МУП \"Электросеть\" целое место. , 1993г., целое место 1985г.","№88 от 24.08.2017"]
[87,"2017-08-15","КЛ-10кВ ПС-\"Поселковая\" яч.11 - ТП-11А  яч.2, ТП-9А яч.4-ТП-13 яч.4 (п. Кадуй)","2017-08-15T17:39:00","2017-08-16T02:27:00",8.7999999998719431,1.2605471999816567,"ЧЛ Куртенко С.Н.   ковшом экскаватора повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление","№87 от 17.08.2017"]
[88,"2017-08-16","КЛ-10кВ РП-1 яч.3 - ТП-18  яч.4","2017-08-16T04:22:00","2017-08-16T04:55:00",0.55000000004656613,0.1019056500086279,"МУП \"Электросеть\" целое место. , 1962г.","№89 от 22.08.2017"]
[89,"2017-08-22","КЛ-10кВ ТП-501 яч.4 - ТП-502  яч.2","2017-08-22T23:21:00","2017-08-23T00:35:00",1.2333333333372138,0.81516796666923153,"МУП \"Электросеть\" каб.разд. , 1968г.","№90 от 29.08.2017"]
[90,"2017-08-24","КЛ-10кВ ГПП-1 яч.15В - РП-1  яч.2","2017-08-24T20:47:00","2017-08-24T20:47:00",0,0,"МУП \"Электросеть\" целое место. , 1962г.","№91 от 07.08.2017"]
[91,"2017-09-02","КЛ-10кВ ГПП-Зашекснинская яч.32 - РП-22  яч.13 (Б)","2017-09-02T23:43:00","2017-09-02T23:43:00",0,0,"МУП \"Электросеть\" целое место. , 1985г.","№92 от 20.09.2017"]
[92,"2017-09-09","КЛ-10кВ ТП-801 яч.5 - ТП-909  яч.3","2017-09-09T16:22:00","2017-09-09T17:06:00",0.73333333345362917,0.42817500007023773,"МУП \"Электросеть\" целое место. , 1978г.","№93 от 15.09.2017"]
[93,"2017-09-08","КЛ-10кВ ТП-1023 яч.4 - ТП-1036  яч.8","2017-09-08T18:55:00","2017-09-08T20:30:00",1.5833333332557231,1.1056638332791369,"ООО \"Немар\"  методом \"ГНБ\" повреждена изоляция КЛ-10кВ. Не получено письменное разрешение на производство работ, не выполнено шурфление","№94 от 20.09.2017"]
[94,"2017-09-11","КЛ-10кВ ТП-217 яч.6 - ТП-218  яч.5","2017-09-11T19:43:00","2017-09-11T21:10:00",1.4499999999922411,0.76308569999591669,"МУП \"Электросеть\" каб.разд. , 1986г.","№95 от 19.09.2017"]
[95,"2017-09-17","КЛ-10кВ ТП-45 яч.3 - ТП-89  яч.3","2017-09-17T07:07:00","2017-09-17T07:54:00",0.78333333336049682,0.16709205000579422,"МУП \"Электросеть\" соед.муфта. , 1989г.","№96 от 27.09.2017"]
[96,"2017-09-20","КЛ-10кВ РП-24 яч.9 - ТП-217  яч.3 ","2017-09-20T19:14:00","2017-09-20T21:25:00",2.183333333329454,2.7943478999950351,"МУП \"Электросеть\" соед.муфта. , 1981г.","№97 от 27.09.2017"]
[97,"2017-09-22","КЛ-10кВ ГПП-4 яч.45 - РП-3  яч.8 (каб. \"В\") ","2017-09-22T22:45:00","2017-09-22T22:45:00",5.8206772735047707E-11,0,"МУП \"Электросеть\" каб.разд. , 1966г.","№98 от 03.10.2017"]
[98,"2017-09-26","КЛ-10кВ ТП-836 яч.4 - ТП-837  яч.8 ","2017-09-26T15:36:00","2017-09-26T16:25:00",0.81666666663174237,0.21171266665761287,"ООО \"Техстрой\" повреждена изоляция КЛ-10кВ методом \"ГНБ\" вследствии отклонения от проектоной схемы","    №99от 27.09.2017"]
[99,"2017-10-02","КЛ-10кВ ГПП-9 яч.408 - РП-17  яч.7 (каб. \"В\")","2017-10-02T10:09:00","2017-10-02T10:09:00",-8.149081409669634E-11,0,"ООО \"Техстрой\"  ковшом экскаватора повреждена изоляция КЛ-10кВ. ","№100 от 06.10.2017"]
[100,"2017-10-02","КЛ-10кВ РП-12 яч.24 - ТП-255  яч.2,                     ТП-254 яч.1-ТП-257 яч.3","2017-10-02T09:37:00","2017-10-02T10:42:00",1.0833333334187039,0.58024200004572501,"МУП \"Электросеть\" целое место. , 1986г., каб.разд. 1984г.","№101 от 06.10.2017"]
[101,"2017-10-10","КЛ-10кВ РП-6 яч.12 - ТП-87  яч.2                   ","2017-10-10T11:00:00","2017-10-10T11:37:00",0.61666666660845904,9.2174399991299588E-2,"МУП \"Электросеть\" целое место. , 1966г.","№102 от 12.10.2017"]
[102,"2017-10-13","КЛ-10кВ ГПП-Искра яч.305 - РП-14  яч.12 (каб. В)                   ","2017-10-13T16:07:00","2017-10-13T16:07:00",2.716493696652833E-11,0,"ООО \"Сити-Девелопмент\"  ковшом экскаватора повреждена изоляция КЛ-10кВ. ","№103 от 13.10.2017"]
[103,"2017-10-13","КЛ-10кВ ГПП-Заягорба яч.112 - РП-8  яч.7 (каб. В)                   ","2017-10-13T18:08:00","2017-10-13T18:08:00",-8.5371709701576037E-11,0,"МУП \"Электросеть\" целое место. , 1966г.","№104 от 23.10.2017"]
[104,"2017-10-17","КЛ-10кВ ТП-361 яч.1 - ТП-362  яч.1                  ","2017-10-17T02:18:00","2017-10-17T03:15:00",0.95000000001164131,0.1908103500023382,"ООО \"Техстрой\"  ковшом экскаватора повреждена изоляция КЛ-10кВ. ","№105 от 24.10.2017"]
[105,"2017-10-23","КЛ-10кВ ГПП-Первомайская яч.105 - РП-28  яч.3                  ","2017-10-23T22:52:00","2017-10-23T22:52:00",2.716493696652833E-11,0,"МУП \"Электросеть\" соед.муфта. , 1998г.","№106 от 26.10.2017"]
[106,"2017-10-28","КЛ-10кВ РП-12 яч.19 - ТП-1812  яч.4                 ","2017-10-28T14:20:00","2017-10-28T14:50:00",0.50000000007761081,0.25846200004011888,"МУП \"Электросеть\" целое место. , 1985г.","№107 от 01.11.2017"]
[107,"2017-10-31","КЛ-10кВ РП-26 яч.17 - ТП-1157  яч.1               ","2017-10-31T10:37:00","2017-10-31T12:57:00",2.3333333333022885,1.989066333306869,"МУП \"Электросеть\" целое место. , 1993г.","№110 от 08.11.2017"]
[108,"2017-10-31","КЛ-10кВ ГПП \"Зашекснинская\"яч.24 - РП-26  яч.1  (каб. \"В\")             ","2017-10-31T10:36:00","2017-10-31T10:36:00",2.3282709094019083E-11,0,"МУП \"Электросеть\" соед.муфта. , 1985г.","№108 от 07.11.2017"]
[109,"2017-10-31","КЛ-10кВ ГПП \"Первомайская\"яч.204 - РП-24  яч.12              ","2017-10-31T12:59:00","2017-10-31T12:59:00",-6.2089000607556954E-11,0,"ООО \"Антей\"  при проведении буровых работ повреждена изоляция КЛ-10кВ. ","№109 от 02.11.2017"]
[110,"2017-10-31","II СШ РУ-10кВ РП-22","2017-10-31T10:36:00","2017-10-31T11:57:00",1.3500000000232819,2.7115155000467626,"МУП \"Электросеть\" каб.разд. , 1964г.","№111от 14.11.2017"]
[111,"2017-11-02","КЛ-10кВ РП-22 яч.18 - КНС №6              ","2017-11-02T09:58:00","2017-11-02T09:58:00",-7.7604589421298442E-12,0,"ООО \"Вектор\"  при проведении земляных работ повреждена изоляция КЛ-10кВ. ","№112 от 08.11.2017"]
[112,"2017-11-16","IСШ РУ-10кВ РП-12","2017-11-16T04:11:00","2017-11-16T04:43:00",0.53333333331781119,0.30558719999110617,"брак (самопроизвольное откл.) ВВ яч.3 РП-12 ООО \"Таврида\"","№113 от 23.11.2017"]
[113,"2017-11-21","КЛ-10кВ РП-25 яч.14 - ТП-149 яч.1                   (каб. \"В\")    ","2017-11-21T21:52:00","2017-11-21T22:20:00",0.46666666663562051,0.2543099999830814,"МУП \"Электросеть\" целое место. , 1992г.","№114 от 28.11.2017"]
[114,"2017-11-22","КЛ-10кВ ГПП Искра яч.305-РП-14 яч.12               (каб \"А\")","2017-11-22T12:09:00","2017-11-22T12:09:00",3.4924063641028624E-11,0,"Брак ПСМО","№115 от 29.11.2017"]
[115,"2017-11-23","КЛ-10кВ РП-22 яч.2 - ТП-1035 яч.3                   ","2017-11-23T14:19:00","2017-11-23T14:44:00",0.41666666662397933,8.3688749991426115E-2,"ИП Егоровым Е.А.  ковшом экскаватора повреждена изоляция КЛ-10кВ. ","№116 от 27.11.2017"]
[116,"2017-11-23","КЛ-10кВ ГПП Искра яч.408-РП-Сев. Котельная              ","2017-11-23T20:06:00","2017-11-23T20:06:00",-3.4924063641028624E-11,0,"МУП \"Электросеть\" соед.муфта. , 1994г.","№117 от 30.11.2017"]
[117,"2017-11-26","КЛ-10кВ РП-25 яч.14 - ТП-149 яч.1                   (каб. \"В\")    ","2017-11-26T20:58:00","2017-11-26T21:36:00",0.63333333326736518,0.45200000000000001,"МУП \"Электросеть\" каб.разд. , 1992г.","№118 от 01.12.2017"]
[118,"2017-11-30","КЛ-10кВ РП-16 яч.11 - ТП-840 яч.3                     ","2017-11-30T22:02:00","2017-11-30T22:25:00",0.38333333328288699,7.6993649989867699E-2,"МУП \"Электросеть\" целое место. , 1984г.","№119 от 18.12.2017"]
[119,"2017-11-30","ТП-206 10/0,4кВ                 ","2017-11-30T19:42:00","2017-11-30T20:30:00",0.80000000004656524,0.26780400001558791,"МУП \"Электросеть\"  силовой тр-р ТП-206 , 2007г.","№120 от 19.12.2017",null,null,0]
[120,"2017-12-07","КЛ-10кВ ГПП-Заягорба  яч.405 - РП-15 яч.2а                     ","2017-12-07T18:34:00","2017-12-07T18:34:00",7.3730355154566496E-11,0,"МУП \"Электросеть\" целое место, 1979г.     ","№122 от 25.12.2017"]
[121,"2017-12-07","КЛ-10кВ ГПП-Заягорба  яч.409 - РП-11 яч.14                     ","2017-12-07T18:34:00","2017-12-07T18:34:00",7.3730355154566496E-11,0,"МУП \"Электросеть\" соед.  муфта, 2007г.     ","№121 от 25.12.2017"]
[122,"2017-12-16","КЛ-10кВ РП-20 яч.14 - ТП-270 яч.6                     ","2017-12-16T02:25:00","2017-12-16T02:54:00",0.4833333333139308,0.16932374999320279,"МУП \"Электросеть\" каб.  разд., 2008г.     ","№123 от 26.12.2017"]
[123,"2017-12-19","КЛ-10кВ РП-23  яч.5 - ТП-МПС яч.1                     ","2017-12-19T10:10:00","2017-12-19T10:10:00",3.8804959245908321E-11,0,"МУП \"Электросеть\" целое место, 1990г.     ","№124 от 27.12.2017"]
[124,"2017-12-24","КЛ-10кВ ГПП-Искра  яч.208 - РП-6 яч.6 (ф.СЖР-5)                     ","2017-12-24T16:40:00","2017-12-24T16:40:00",-1.9400481221509835E-11,0,"МУП \"Электросеть\" целое место, 1990г.     ","№125 от 28.12.2017"]
[125,"2017-12-24","КЛ-10кВ РП-6 яч.16 - ТП-108 яч.2              КЛ-10кВ ТП-145 яч.4 - ТП-146 яч.1                   ","2017-12-24T15:50:00","2017-12-24T16:50:00",1.000000000077609,0.13779400001069408,"МУП \"Электросеть\" каб.  разд., 2008г.     ","№126 от 28.12.2017"]
[126,"2017-12-27","КЛ-10кВ РП-15 яч.5 - ТП-253 яч.4                     ","2017-12-27T12:27:00","2017-12-27T12:58:00",0.5166666665968167,0.15807416664529605,"МУП \"Электросеть\" каб.  разд., 2008г.     ","№127 от 12.01.2018"]
[127,"2017-12-27","КЛ-10кВ ТП-245 яч.7 - ТП-249 яч.5                     ","2017-12-27T12:27:00","2017-12-27T13:30:00",1.0499999999301508,0.21089564998597057,"МУП \"Электросеть\" целое место, 1982г.     ","№128 от 12.01.2018"]