{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["2023"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"2023","index":0,"n_rows":37,"n_cols":9,"rows_kept":37,"cut":false,"hidden":false,"merged":[[1,0,1,8]]}
[]
["                    Статистика актов расследования причин аварии 2023г."]
[]
["Кол-во отказавшего оборудования","Дата","Место","Время начала (часы, мин., год, день, мес.)","Время устранения аварийного режима (часы, мин., год, день, мес.)","Время простоя (час)","Недоотпуск эл. энергии (тыс. кВт*час)","Причина возникновения","№   акта расследования причин аварии"]
[1,"2023-01-25","КЛ-10кВ ТП-252 яч.4--ТП-248 яч.4","2023-01-25T08:57:00","2023-01-25T09:58:00",1.0166666666550257,0.25397553333042527,"МУП \"Электросеть , целое место,  старение изоляции "," №1 30.01.2023"]
[2,"2023-02-09","ТП-317  - ТП-320","2023-02-09T07:32:00","2023-02-09T08:17:00",0.75000000006596856,0.12572775001105876,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №2 13.02.2023"]
[3,"2023-02-20","РП-7яч.5- ТП-1612яч.1","2023-02-20T21:56:00","2023-02-20T22:16:00",0.33333333325960179,0.23534933328127533,"МУП \"Электросеть\",  соед. муфта,  старение изоляции ","№3 20.02.2023"]
[4,"2023-03-21","ТП-549 яч.1 - ТП-543 яч.2","2023-03-21T01:37:00","2023-03-21T02:55:00",1.2999999999689558,0.26664169999363257,"МУП \"Электросеть , целое место,  старение изоляции ","№4 30.03.2023"]
[5,"2023-03-21","ГПП Зашекснинская яч.26 - ТП КОСК ЛБУ яч.3 (ф.ЗОС-1)","2023-03-21T02:34:00","2023-03-21T02:34:00",1.5521917084981851E-11,0,"МУП \"Электросеть , целое место,  старение изоляции ","№5 30.03.2023"]
[6,"2023-03-27","РП 28 яч.19 -- ТП 2315 яч.3","2023-03-27T18:26:00","2023-03-27T19:00:00",0.56666666665114374,0.28218866665893655,"МУП \"Электросеть\" каб.разд , резкие перепады температурного режима воздуха  "," №6 04.04.2023"]
[7,"2022-03-29","РП-26 яч.1 СВВ","2022-03-29T15:28:00","2022-03-29T16:29:00",1.0166666667171134,3.5509787668428654,"МУП \"Электросеть\" попадание крысы на СВВ яч.1 РП-26","№7 03.04.2023"]
[8,"2023-04-13","ТП-548 яч.1 - ТП-11511 яч.3","2023-04-13T07:15:00","2023-04-13T07:40:00",0.41666666660845975,0.26898624996242354,"МУП \"Электросеть , целое место,  старение изоляции "," №8 24.04.2023"]
[9,"2023-04-16","ТП-605 яч.2 - ТП-410 яч.3","2023-04-16T09:26:00","2023-04-16T10:00:00",0.56666666665114507,0.28690503332547468,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №9 26.04.2023"]
[10,"2023-04-17","ТП-58А яч.2 - ТП-21 яч.3","2023-04-17T16:02:00","2023-04-17T16:35:00",0.54999999994955306,7.999749999266248E-2,"МУП \"Электросеть , целое место,  старение изоляции "," №10 02.05.2023"]
[11,"2023-04-29","РП-13яч.11 - ТП-115яч.4","2023-04-29T12:10:00","2023-04-29T12:39:00",0.48333333331393113,3.2568933332025936E-2,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №11 05.05.2023"]
[12,"2023-04-30","ТП-337 яч.1 - ТП-323 яч.4","2023-04-30T12:23:00","2023-04-30T12:58:00",0.58333333330616899,0.1438062499933033,"ООО \"ИнвестСтрой\" ,брак при монтаже"," №12 10.05.2023"]
[13,"2023-05-18","РТП-4 яч.8 - ТП-332 яч.5","2023-05-18T01:11:00","2023-05-18T01:30:00",0.31666666665114462,0.17518063332474651,"Брак при монтаже ООО \"Череповецэлектроплюс\" "," №13 28.05.2023"]
[14,"2023-05-22","ТП-243 яч.2 - ТП-244 яч.3","2023-05-22T20:59:00","2023-05-22T21:40:00",0.68333333338766078,0.22438685001783956,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №14 28.05.2023"]
[15,"2023-06-02","ТП-215 - ТП-216","2023-06-02T11:29:00","2023-06-02T11:50:00",0.34999999993791242,0.20420504996377542,"МУП \"Электросеть\" каб.разд , резкие перепады температурного режима воздуха  "," №15 05.06.2023"]
[16,"2023-06-07","ТП-270 яч.3--ТП-273 яч.3","2023-06-07T08:59:00","2023-06-07T09:25:00",0.43333333338766034,3.7959566671425665E-2,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №16 14.06.2023"]
[17,"2023-06-07","ТП 57 яч 4 - ТП 105 яч 4","2023-06-07T16:25:00","2023-06-07T16:56:00",0.51666666658905758,0.23181593329851199,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №17 14.06.2023"]
[18,"2023-06-14","КТПН-5 яч.1 - оп.№57","2023-06-14T18:15:00","2023-06-14T19:30:00",1.2500000000582077,0.75600000000000001,"МУП \"Электросеть\" каб.разд , резкие перепады температурного режима воздуха  "," №18 19.06.2023"]
[19,"2023-06-30","ГПП-1 яч.3Б--РП-16 яч.1","2023-06-30T20:06:00","2023-06-30T20:06:00",-3.4924063641028624E-11,0,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №19 04.07.2023"]
[20,"2023-07-19","РП-24 яч.11-ТП-1610 яч.4","2023-07-19T13:09:00","2023-07-19T13:40:00",0.51666666658517535,0.1242293999804059,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №20 27.07.2023"]
[21,"2023-08-08","ТП-27 яч.2 - ТП-905 яч.5","2023-08-08T03:32:00","2023-08-08T04:17:00",0.75000000000776113,0.58426425000604609,"МУП \"Электросеть , целое место,  старение изоляции "," №21 23.08.2023"]
[22,"2023-08-22","ТП-181яч.1- ТП-182яч.2","2023-08-22T11:06:00","2023-08-22T11:40:00",0.56666666663174192,0.34272453331221053,"МУП \"Электросеть , целое место,  старение изоляции "," №22 30.08.2023"]
[23,"2023-09-13","ТП-20 яч.1 - ТП-25 яч.1","2023-09-13T14:35:00","2023-09-13T15:12:00",0.61666666662786085,0.12080808332573108,"МУП \"Электросеть , целое место,  старение изоляции "," №23 29.09.2023"]
[24,"2023-09-14","ТП-27 яч.4 - ТП-901 яч.2","2023-09-14T11:50:00","2023-09-14T12:33:00",0.71666666668606993,0.50706101668039505,"Неустановленнные лица,  мех.повр. арматурой, повреждение изоляции КЛ-10кВ"," №24 20.09.2023"]
[25,"2023-09-22","РП-24 яч.18 - ТП-208 яч.5","2023-09-22T20:50:00","2023-09-22T21:18:00",0.46666666668607082,0.53074093335540173,"МУП \"Электросеть , целое место,  старение изоляции "," №25 09.10.2023"]
[26,"2023-09-24","ТП-451яч.7-ТП-2711оп.№1","2023-09-24T10:10:00","2023-09-24T11:10:00",1.0000000000388041,0.22290000000864943,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №26 09.10.2023"]
[27,"2023-10-07","ТП-272 яч.6-ТП-273 яч.6","2023-10-07T17:40:00","2023-10-07T19:35:00",1.9166666667054715,0.42808750000866708,"ООО \"ИммидСтрой\",  мех.повреждение"," №27 14.10.2023"]
[28,"2023-10-21","РТП-4 яч.15--ТП-389 яч.2","2023-10-21T15:35:00","2023-10-21T15:56:00",0.3500000000194019,9.8708750005471815E-2,"Брак при монтаже ООО \"Череповецэлектроплюс\" "," №28 23.10.2023"]
[29,"2023-11-14","ТП-244 - ТП-2510","2023-11-14T02:57:00","2023-11-14T03:59:00",1.0333333333216916,0.23640083333067,"МУП \"Электросеть , целое место,  старение изоляции "," №29 21.11.2023"]
[30,"2023-11-16","ТП-320 яч.2-ТП-317 яч.2","2023-11-16T13:02:00","2023-11-16T13:48:00",0.76666666661622163,0.19656259998706663,"МУП \"Электросеть , целое место,  старение изоляции "," №30 22.11.2023"]
[31,"2023-11-18","ТП-903 яч.5","2023-11-18T11:13:00","2023-11-18T11:45:00",0.53333333326736421,0.63027359992204002,"МУП \"Электросеть\" ,в/в предохранители"," №31 04.12.2023"]
[32,"2023-11-21","ТП-272 - ТП-273","2023-11-21T17:07:00","2023-11-21T18:10:00",1.0500000000853733,0.96031110007808096,"МУП \"Электросеть\",  соед. муфта,  старение изоляции "," №32 05.12.2023"]
[33,"2023-11-25","РП-3 яч.17-ТП-381 яч.4","2023-11-25T09:08:00","2023-11-25T09:50:00",0.6999999999146298,0.41198219994975571,"МУП \"Электросеть , целое место,  старение изоляции "," №33 06.12.2023"]