{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["1"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"1","index":0,"n_rows":75,"n_cols":9,"rows_kept":75,"cut":false,"hidden":false,"merged":[[1,0,1,8],[81,0,81,2]]}
[]
["                    Статистика актов расследования причин аварии 2019г."]
[]
["Кол-во отказавшего оборудования","Дата","Место","Время начала (часы, мин., год, день, мес.)","Время устранения аварийного режима (часы, мин., год, день, мес.)","Время простоя (час)","Недоотпуск эл. энергии (тыс. кВт*час)","Причина возникновения","№   акта расследования причин аварии"]
[1,"2019-01-01","ГПП- Зашекснинская  яч.13 - РП-22 яч.6 (каб. \"А\", \"В\") ","2019-01-01T19:01:00","2019-01-01T19:01:00",3.879563337250147E-12,0,"МУП \"Электросеть\" ,целое место., 1987г., целое место., 1987г., соед.муфта - 3СС-100, 1987г., старение изоляции ","№1            17.01.2019"]
[2,"2019-01-01","ТП-98 яч.5 - ТП-106 яч.2","2019-01-01T20:48:00","2019-01-01T22:40:00",1.8666666666201026,0.80042666664670004,"МУП \"Электросеть\" ,каб.разд., 3КВТП 10-70/120 2007г., старение изоляции","№2   17.01.2019"]
[3,"2019-01-01","ГПП- Зашекснинская  яч.24 - РП-26 яч.11 (каб.  \"В\") ","2019-01-01T23:20:00","2019-01-01T23:20:00",7.7609918491816643E-11,0,"МУП \"Электросеть\" ,соед.муфта., 1991г., старение изоляции ","№3                17.01.2019"]
[4,"2019-01-16","ГПП- Первомайская  яч.102 - РП-24 яч.3 ","2019-01-16T18:49:00","2019-01-16T18:49:00",-4.2685854850788019E-11,0,"МУП \"Электросеть\" ,соед.муфта., 1985г., старение изоляции ","№4             22.01.2019"]
[5,"2019-01-28","РП- 28  яч.18 - ТП-2317 яч.3 ","2019-01-28T01:20:00","2019-01-28T01:48:00",0.46666666668606915,1.416893333392243E-2,"МУП \"Электросеть\" ,соед.муфта., 1979г., старение изоляции ","№5             01.02.2019"]
[6,"2019-01-29","РП- 25  яч.14 - ТП-149 яч.1 (каб.В) ","2019-01-29T09:14:00","2019-01-29T10:45:00",1.5166666666045789,1.0555696666234549,"МУП \"Электросеть\" ,целое место., 1992г., старение изоляции ","№6              15.02.2019"]
[7,"2019-02-08","ГПП- Искра  яч.205 - РП-14 яч.12 (каб. \"В\") ","2019-02-08T02:36:00","2019-02-08T02:36:00",8.149081409669634E-11,0,"МУП \"Электросеть\" соединительная муфта, 2014г., дефект монтажа ООО \"ПСМО\"( замена за счет МУП \"Электросеть\")","№7             15.02.2019"]
[8,"2019-02-12","оп. №6А - КТПН- \"Судский рейд\" яч.1 (п. Кадуй)","2019-02-12T23:49:00","2019-02-13T01:34:00",1.7500000000737299,1.2859997500541809,"МУП \"Электросеть\" ,каб. разд оп. 6А ВЛ-10кВ., 1979г., воздействие неблагоприятных природных явлений ","№8                26.02.2019"]
[9,"2019-02-20","РП- 11  яч.10 - ТП-220 яч.2","2019-02-20T19:25:00","2019-02-20T19:45:00",0.33333333325572223,4.0481999990574447E-2,"МУП \"Электросеть\" ,целое место., 1976г., старение изоляции ","№9                05.03.2019"]
[10,"2019-02-21","ТП- 1023 яч.4 - ТП-1024 яч.4","2019-02-21T09:28:00","2019-02-21T11:17:00",1.8166666667171132,0.7572030166876933,"МУП \"Электросеть\" ,каб. разд яч. 4 ТП-1024., 2008г., воздействие неблагоприятных природных явлений ","№10 05.03.2019"]
[11,"2019-03-12","ТП- 1041 яч.5 - ТП-1151 яч.4","2019-03-12T21:53:00","2019-03-12T22:36:00",0.71666666658129774,1.4568536164931269,"МУП \"Электросеть\" ,целое место., 1991г., старение изоляции ","№11 18.03.2019"]
[12,"2019-03-25","ТП- 451 яч.5 - ТП-272 яч.3","2019-03-25T01:23:00","2019-03-25T01:50:00",0.45000000003104423,0.21368700001474167,"ООО \"КапЭнергСстрой\" ,целое место., 2017г., брак при монтаже","№12 01.04.2019"]
[13,"2019-04-01","РП- 11 яч.10 - ТП-220 яч.2 (участок в месте повреждения на балансе МУП \"Электросеть\" не числится","2019-04-01T13:59:00","2019-04-01T14:20:00",0.34999999999611919,2.8882349999679754E-2,"ООО \"Энергостройсервис\" ,целое место., 2018г., (вынос из зоны строительства) повреждение при прокладке водовода, КЛ  на балансе МУП \"Электросеть\" не числится","№13 09.04.2019"]
[14,"2019-04-11","ГПП- 9 яч.408 - РП-17 яч.7 (каб.А)","2019-04-11T08:55:00","2019-04-11T08:55:00",-7.7611250759446193E-11,0,"МУП \"Электросеть\" ,кабельная разделка 3КВТП-10-150/240., 1995г., старение изоляции ","№14 22.04.2019"]
[15,"2019-04-11","ТП- 46 яч.1 - ТП-45 яч.1","2019-04-11T15:48:00","2019-04-11T16:25:00",0.61666666667830849,0.202399250003821,"МУП \"Электросеть\" ,соед.муфта., 2016г., брак при монтаже ООО ПКФ \"Антей\"","№15 23.04.2019"]
[16,"2019-04-15","ТП- 205 яч.2 - ТП-215 яч.3","2019-04-15T03:02:00","2019-04-15T04:05:00",1.0500000000659682,0.40217310002526729,"ЧЛ  Патраков С.В. ,целое место., 1986г.,  мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.","№16 24.04.2019"]
[17,"2019-04-23","ТП- 113 яч.3 - ТП-149 яч.6","2019-04-23T08:27:00","2019-04-23T09:22:00",0.91666666671323283,0.52094625002646378,"ООО \"Невалестрой\". ,целое место., 1992г.,  мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ. ","№17 25.04.2019"]
[18,"2019-04-29","ТП- 177 яч.4 - ТП-182 яч.5","2019-04-29T18:11:00","2019-04-29T18:55:00",0.7333333332596057,0.23806566664273207,"СПМ-Центр ,целое место., 1970г.,  мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ. ","№18 06.05.2019"]
[19,"2019-05-01","ТП- 226 яч.4 - ТП-229 яч.4","2019-05-01T23:10:00","2019-05-01T23:55:00",0.74999999992239008,0.51264224994695184,"МУП \"Электросеть\" ,целое место.,  1976г., старение изоляции ","№19 08.05.2019"]
[20,"2019-05-11","РП- 11 яч.12 - ТП-2010 яч.6","2019-05-11T11:34:00","2019-05-11T11:52:00",0.30000000001552252,6.3992700003311087E-2,"МУП \"Электросеть\" ,каб. разд яч. 6 ТП-2010., 1982г., воздействие неблагоприятных природных явлений (резкие перепады температурного режима воздуха) ","№20 20.05.2019"]
[21,"2019-05-15","РП- 6 яч.12 - ТП-87 яч.2","2019-05-15T01:27:00","2019-05-15T02:10:00",0.7166666666550251,5.5234574999102767E-2,"МУП \"Электросеть\" ,целое место.,  1966г., старение изоляции","№21 27.05.2019"]
[22,"2019-05-16","ТП- 225 яч.4 - ТП-222 яч.4","2019-05-16T02:59:00","2019-05-16T03:40:00",0.68333333338766011,0.1457611500115884,"МУП \"Электросеть\" ,целое место.,  1973г., (коррозия ). Снижение эл.прочности и естественное старение изоляции","№22 22.05.2019"]
[23,"2019-05-16","ГПП- Первомайская яч.204 - РП-24 яч.12","2019-05-16T03:00:00","2019-05-16T03:00:00",0,0,"МУП \"Электросеть\" ,соед.муфта.,  1991г.,(коррозия ). Снижение эл.прочности и естественное старение изоляции","№23 24.05.2019"]
[24,"2019-05-17","ТП- 844 яч.5 - ТП-840 яч.1                                     ТП-844 яч.2 - ТП-842 яч.7","2019-05-17T13:09:00","2019-05-17T15:30:00",2.3499999999185102,0.45005084998439376,"ООО \"Гермес\" ,целое место., 1985г. ТП-840-ТП-844,  целое место., 1985г. ТП-842-ТП-844  по ул. Маяковского, 10, мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.  ","№24 08.05.2019"]
[25,"2019-05-24","РП- 26 яч.18 - ТП-554 яч.1                                     ТП-554 яч.6 - ТП-553 яч.4","2019-05-24T10:07:00","2019-05-24T12:35:00",2.4666666666938308,0.69361186667430519,"СКА \"Города\" ,целое место., 2007г. РП- 26 яч.18 - ТП-554 яч.1      целое место., 2007г. ТП-554 яч.6 - ТП-553 яч.4 по ул. Рыбинская, 59, мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.  ","№25 28.05.2019"]
[26,"2019-05-24","РП- 10 яч.5 - ТП-124 яч.2                                     ","2019-05-24T15:08:00","2019-05-24T15:58:00",0.83333333324796133,0.17256749998232107,"МУП \"Электросеть\" ,соед.муфта,  1971г., (коррозия ). Снижение эл.прочности и естественное старение изоляции","№26 29.05.2019"]
[27,"2019-05-24","   ТП-109 яч.5 - ТП-4 яч.1","2019-05-24T15:10:00","2019-05-24T15:35:00",0.41666666664726471,5.8387499997281204E-2,"СКА \"Города\" ,целое место., 1969г. ТП-109 яч.5 - ТП-4 яч.1 по ул. Белинского, 4, мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.  ","№27 29.05.2019"]
[28,"2019-05-28","ТП-20 яч.1-ТП-25 яч.1                                            ТП-21 яч.3-ТП-58а яч.2","2019-05-28T17:05:00","2019-05-28T19:33:00",2.466666666686069,0.2938046666689777,"МУП \"Электросеть\" ,целое место.,  1986г., соед.муфта, 1989 (коррозия ). Снижение эл.прочности и естественное старение изоляции","№28 13.06.2019"]
[29,"2019-06-08","ТП-384 яч.2-ТП-387 яч.3                                            ","2019-06-08T18:47:00","2019-06-08T19:50:00",1.0500000000659675,0.60816420003820859,"МУП \"Электросеть\" каб.разд , 'битум., 1964г.,воздействие неблагоприятных природных явлений ","№29 11.06.2019"]
[30,"2019-06-09","ТП-49 яч.4-ТП-62 яч.2                                            ","2019-06-09T18:19:00","2019-06-09T18:57:00",0.63333333334885467,0.26624700000652501,"МУП \"Электросеть\" ,каб.разд.,  1968г. эпокс. (нарушение герметичности кабельных разделок, износ) ","№30 17.06.2019"]
[31,"2019-06-19","ТП-150А яч.4 - ТП-1272 яч.12                                      ТП-150А яч.3-ТП-1271 яч.2","2019-06-19T17:35:00","2019-06-19T18:08:00",0.54999999996119442,9.0463999993617247E-2,"Частное лицо, Смышляев А.И., целое место., 2015г., 2015г.,  мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.  ","№31 26.06.2019"]
[32,"2019-06-21","РП-10 яч.13-ТП-2015 яч.2                                            ","2019-06-21T07:50:00","2019-06-21T08:39:00",0.81666666662786147,0.13859894999341424,"МУП \"Электросеть\" ,целое место.,  1989г. (коррозия ). Снижение эл.прочности и естественное старение изоляции","№32 26.06.2019"]
[33,"2019-06-27","ТП-189 яч.1-ТП-1811 яч.1                                            ","2019-06-27T10:07:00","2019-06-27T10:37:00",0.50000000002716449,2.6296000001428635E-2,"ООО  \"Череповецэлектроплюс\",мех.повр.,  1983г. ","№33 28.06.2019"]
[34,"2019-07-29","ТП-388 яч.1-ТП-311 яч.5                                            ","2019-07-29T16:15:00","2019-07-29T17:10:00",0.9166666666084593,0.29686799998114916,"МУП \"Электросеть\" ,целое место.,  1963г. (коррозия ). Снижение эл.прочности и естественное старение изоляции","№34 07.08.2019"]
[35,"2019-08-03","РП-2 яч.12-ТП-702 яч.1                                            ","2019-08-03T13:09:00","2019-08-03T13:30:00",0.34999999991850927,6.3759149985154917E-2,"ИП Белянкин С.В., целое место, 2019г., мех.повреждение бурильной установкой, повреждение изоляции КЛ-10кВ.  ","№35 07.08.2019"]
[36,"2019-08-05","ТП-1152 яч.2-ТП-1155 яч.4                                            ","2019-08-05T20:21:00","2019-08-05T21:35:00",1.2333333333566143,0.8679756000163843,"МУП \"Электросеть\" каб.разд , 'битум., 1999г.,заплывающий пробой","№36 13.08.2019"]
[37,"2019-08-14","ГПП-Первомайская яч.303-РП-10 яч.8                                            ","2019-08-14T10:38:00","2019-08-14T10:38:00",-8.5371709701576037E-11,0,"ООО \"СК-Города\", целое место, 1998г., мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ. ","№37 16.08.2019"]
[38,"2019-08-22","РП-13 яч.8-ТП-141 яч.3                                            ","2019-08-22T18:42:00","2019-08-22T19:16:00",0.5666666666550233,0.13058039999731696,"МУП \"Электросеть\" , соед.муфта, 1989г. (коррозия ). Снижение эл.прочности и естественное старение изоляции","№38 28.08.2019"]
[39,"2019-08-26","ТП-6 яч.3-ТП-5 яч.3                                            ","2019-08-26T09:46:00","2019-08-26T11:34:00",1.7999999999456731,0.2746547999917105,"фл Нерубацкий Д.Н., целое место, 1963г., мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.  ","№39 29.08.2019"]
[40,"2019-08-26","ТП-65 яч.2-ТП-41 яч.1                                            ","2019-08-26T18:30:00","2019-08-26T19:20:00",0.8333333332751236,0.28934249997978895,"МУП \"Электросеть\" ,целое место.,  1978г. (коррозия). Снижение эл.прочности и естественное старение изоляции","№40 02.09.2019"]
[41,"2019-09-03","ТП-6 яч.3-ТП-5 яч.4                                            ","2019-09-03T16:57:00","2019-09-03T17:30:00",0.54999999993014992,8.3922299989341864E-2,"фл Нерубацкий Д.Н., целое место, 1963г., мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.  ","№41 11.09.2019"]
[42,"2019-09-03","ТП-76 яч.1-ТП-29 яч.6                                            ","2019-09-03T19:10:00","2019-09-03T19:45:00",0.58333333337213755,4.2233333336142764E-2,"ООО Строительные технологии, целое место, 1962г., мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ.  ","№42 12.09.2019"]
[43,"2019-09-03","ТП-705 яч.2-ТП-702 яч.2                                            ","2019-09-03T17:27:00","2019-09-03T18:15:00",0.80000000004656524,0.17625200001025904,"ООО \"Артель-Групп\" ,целое место., 2019г., брак при монтаже","№43 13.09.2019"]
[44,"2019-09-24","РП-26 яч.23-ТП-551 яч.2                                            ","2019-09-24T20:16:00","2019-09-24T20:45:00",0.48333333327900707,5.1474516660880973E-2,"МУП \"Электросеть\" ,целое место.,  1994г., (коррозия ). Снижение эл.прочности и естественное старение изоляции","№44 01.10.2019"]
[45,"2019-09-25","ТП-701 яч.4-ТП-1 яч.4                                            ","2019-09-25T15:44:00","2019-09-25T16:52:00",1.1333333333876618,0.63702060003053684,"ООО \"Стройпроект\" ,целое место., 1971г., мех.повреждение ковшом бульдозера, повреждение изоляции КЛ-10кВ.  ","№46 02.10.2019"]
[46,"2019-09-26","ТП-89 яч.5-ТП-91 яч.3                                            ","2019-09-26T03:27:00","2019-09-26T04:45:00",1.2999999999301506,0.37243439997998901,"МУП \"Электросеть\" ,целое место.,  1970г., (коррозия ). Снижение эл.прочности и естественное старение изоляции","№45 08.10.2019"]
[47,"2019-09-27","РП-8 яч.10-ТП-9 яч.1                                            ","2019-09-27T15:40:00","2019-09-27T16:04:00",0.39999999992238866,0.23479559995444302,"ООО \"СК-Арбат\" ,целое место., 1966г., мех.повреждение ковшом бульдозера, повреждение изоляции КЛ-10кВ.  ","№47 04.10.2019"]
[48,"2019-10-01","ТП-277 яч.6-ТП-279 яч.6                                            ","2019-10-01T09:49:00","2019-10-01T10:48:00",0.98333333329064798,0.15815736665980124,"АО \"ГазпромГазораспределение Вологда\" ,целое место., 2008г., мех.повреждение ковшом экскаватра, повреждение изоляции КЛ-10кВ.  ","№48 10.10.2019"]
[48,"2019-10-05","ТП-1442 яч.2-ТП-11214 яч.6                                            ","2019-10-05T16:10:00","2019-10-05T16:45:00",0.58333333337213755,0.85811425005708319,"ИП Карпов Д.Н. ,целое место., 1981г., мех.повреждение ковшом экскаватра, повреждение изоляции КЛ-10кВ.  ","№49 16.10.2019"]
[50,"2019-10-13","ТП-1159 яч.1-ТП-11510 яч.4                                            ","2019-10-13T20:00:00","2019-10-13T20:48:00",0.79999999994179305,0.91177919993366008,"МУП \"Электросеть\" ,соед. муфта,   2003г. (коррозия). Снижение эл.прочности и естественное старение изоляции. ","№50 15.10.2019"]
[51,"2019-10-15","ТП-273 яч.6-ТП-272 яч.6                                            ","2019-10-15T13:49:00","2019-10-15T14:50:00",1.0166666666821893,0.3115249666714231,"ООО «ИммидСтрой» ,целое место, 2010г., мех.повреждение ковшом экскаватра, повреждение изоляции КЛ-10кВ.  ","№51 24.10.2019"]
[52,"2019-10-15","РП-26 яч.24-РП-36 яч.5                                            ","2019-10-15T15:11:00","2019-10-15T16:16:00",1.0833333332596018,2.2163894998491527,"МУП \"Электросеть\" , целое место, 2018г, брак при монтаже  ООО Строительная компания «Стройинвест», РП-26 яч.24 ВВ не отключился брак завода-изготовителя","№52 01.11.2019"]
[53,"2019-10-20","ТП-54 яч.2 - ТП-6 яч.5                                            ","2019-10-20T11:20:00","2019-10-20T12:25:00",1.0833333334109421,0.23445825001679632,"МУП \"Электросеть\" ,соед. муфта,   1974г. (коррозия ). Снижение эл.прочности и естественное старение изоляции. ","№53 04.11.2019"]
[54,"2019-10-26","ТП-272 яч.1 - ТП-275 яч.3                                            ","2019-10-26T20:35:00","2019-10-26T21:25:00",0.83333333329452941,0.36667333331625929,"МУП \"Электросеть\" ,целое место,   2011г. (коррозия). Снижение эл.прочности и естественное старение изоляции. ","№54 05.11.2019"]
[55,"2019-10-30","ТП-2510 яч.1 - ТП-258 яч.4                                            ","2019-10-30T01:00:00","2019-10-30T01:50:00",0.83333333339154114,0.23614500001649461,"МУП \"Электросеть\" ,  целое место,  1984г,(коррозия ). Снижение эл.прочности и естественное старение изоляции","№55 04.11.2019"]
[56,"2019-11-02","РП-22 яч.18 - КНС-6 ввод №2                                            ","2019-11-02T07:44:00","2019-11-02T07:44:00",-6.2087668339927404E-11,0,"Брак при монтаже ООО \"Пром-Альянс\" ,  соед.муфта,  2017г, поврежденный участок КЛ-10кВ (вставка-вынос из зоны строительства торгового комплекса Леруа) на балансе МУП \"Электросеть\" не числится). ","№56 12.11.2019"]
[57,"2019-11-11","ГПП-Заягорба яч.112 - РП-8 яч.7 (каб. \"В\")                 ф. \"ФБТ-1\"                                            ","2019-11-11T04:53:00","2019-11-11T04:53:00",-2.7164270832713555E-11,0,"МУП \"Электросеть\" ,  соед.муфта,  1966г, (коррозия ). Снижение эл.прочности и естественное старение изоляции. ","№57 14.11.2019"]
[58,"2019-11-17","ТП-10 яч.7 - оп.№53  ф. \"Винзавод\"                      (п. Кадуй)","2019-11-17T14:30:00","2019-11-17T14:50:00",0.33333333339154159,4.3066666674187168E-2,"МУП \"Электросеть\" , Кадуй, ВЛ-10кВ, целое место,   1982г., старение изоляции ","№58 04.12.2019"]
[59,"2019-11-19","ПС-Зашекснинская яч.24 - РП-26 яч.11                        (каб. \"А\", \"В\")   ф. \"ЗЖР-3\"                                            ","2019-11-19T00:05:00","2019-11-19T00:05:00",7.7610209925360607E-11,0,"МУП \"Электросеть\" ,  каб. \"А\" - соед.муфта,  1994г, каб. \"В\" - соед.муфта,  1984г,  старение изоляции (механические воздействия вследствие подвижек грунта)","№59 06.12.2019"]
[60,"2019-11-23","ТП-92 яч.1 - ТП-34 яч.4                                            ","2019-11-23T02:27:00","2019-11-23T03:33:00",1.1000000000465662,0.21699810000918615,"МУП \"Электросеть\" ,  целое место,  1971г,старение изоляции (механические воздействия вследствие подвижек грунта)","№60 05.12.2019"]
[61,"2019-11-23","ГПП-9 яч.310 - РП-14 яч.4 (каб. \"А\")                                            ","2019-11-23T02:28:00","2019-11-23T02:52:00",0.39999999999223912,0.30853479999401373,"МУП \"Электросеть\" ,целое место., 2007г., старение изоляции ","№61 05.12.2019"]
[62,"2019-11-26","РП-24 яч.6 - ТП-2016 яч.2                                            ","2019-11-26T09:26:00","2019-11-26T10:27:00",1.0166666666511435,0.23744249999637457,"МУП \"Электросеть\" ,соед.муфта., 2004г., старение изоляции ","№62 06.12.2019"]
[63,"2019-11-27","ТП-2316 яч.2 - ТП-2320 яч.2                                            ","2019-11-27T03:15:00","2019-11-27T04:02:00",0.78333333339154065,0.25002825001857892,"МУП \"Электросеть\" ,целое место, 2015г., дефект монтажа ООО ПСМО, замена за счет МУП \"Электросеть\")","№63 04.11.2019"]
[64,"2019-12-04","ГПП-9 яч.311 - РП-2 яч.23 (каб. \"В\")                                            ","2019-12-04T14:55:00","2019-12-04T15:04:00",0.14999999992238955,0.24803009987166849,"МУП \"Электросеть\" ,  соед.муфта,  2006г,старение изоляции ","№64 11.12.2019"]
[65,"2019-12-09","РП-1 яч.5 - ТП-376 яч.1                                            ","2019-12-09T09:54:00","2019-12-09T10:58:00",1.0666666667015909,0.56550293335184865,"МУП \"Электросеть\" ,  целое место,  1956г,старение изоляции ","№65 15.12.2019"]
[66,"2019-12-16","ГПП-9 яч.107 - РП-36 яч.9                                            ","2019-12-16T19:53:00","2019-12-16T19:53:00",-2.716493696652833E-11,0,"МУП \"Электросеть\" ,  целое место,  1985г,старение изоляции ","№66 11.12.2019"]
[67,"2019-12-19","РП-15 яч.9 - ТП-174 яч.1а                                             ","2019-12-19T02:34:00","2019-12-19T03:00:00",0.43333333334885538,4.8578400001740088E-2,"МУП \"Электросеть\" ,  целое место,  1979г,старение изоляции ","№67 24.12.2019"]
[68,"2019-12-20","ГПП-Зашекснинская яч.24 - РП-26 яч.11 (ф.ЗЖР-3) каб. \"В\"                                            ","2019-12-20T20:18:00","2019-12-20T20:18:00",1.1641354547009541E-11,0,"МУП \"Электросеть\" ,  целое место, 1985г,старение изоляции ","№68 23.12.2019"]
[69,"2019-12-24","ТП-2314 яч.3 - ТП-2316 яч.3                                             ","2019-12-24T02:28:00","2019-12-24T03:35:00",1.1166666666589056,0.46839141666341122,"МУП \"Электросеть\" ,  целое место,  1980г,старение изоляции ","№69 24.12.2019"]
[70,"2019-12-24","откл. яч.16 РУ-10кВ РП-10, ТП- 13  яч.6 -течь кровли","2019-12-24T22:37:00","2019-12-25T00:57:00",2.3333333333022894,4.3595999999419981E-2,"МУП \"Электросеть\" ,течь кровли ТП-13, повреждение опорного изолятора (ф.\"С\") яч.6 РУ-10кВ ТП-13, отсутствие надлежащего контроля и ремонта строительной части ТП-13 ОАО \"Череповецкий порт\" ","№70 25.12.2019"]
[71,"2019-12-25","ТП-1815 яч.3 - ТП-1816 яч.4","2019-12-25T01:15:00","2019-12-25T02:10:00",0.91666666660845897,0.17469558332224028,"МУП \"Электросеть\" ,  целое место,  1991г,старение изоляции "," №71 17.12.2019"]