{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["2022"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"2022","index":0,"n_rows":35,"n_cols":9,"rows_kept":35,"cut":false,"hidden":false,"merged":[[1,0,1,8]]}
[]
["                    Статистика актов расследования причин аварий 2022г."]
[]
["Порядковый №","Дата","Место","Время начала (часы, мин., год, день, мес.)","Время устранения аварийного режима (часы, мин., год, день, мес.)","Время простоя (час)","Недоотпуск эл. энергии (тыс. кВт*час)","Причина возникновения","№   акта расследования причин аварии"]
[1,"2022-01-31","РП-2 яч.11 -- ТП-133 яч.4","2022-01-31T05:00:00","2022-01-31T05:40:00",0.66666666660845952,2.629333333103764E-2,"МУП \"Электросеть\",выход из строя  вследствие подвижек грунта"," №1 07.02.2022"]
[2,"2022-03-17","РП-28 яч.9--ТП-238 яч.3","2022-03-17T20:34:00","2022-03-17T21:04:00",0.50000000001552181,9.6966500003010186E-2,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта"," №2 25.03.2022"]
[3,"2022-03-18","ТП-901 яч.4 - ТП-808 яч.3","2022-03-18T10:30:00","2022-03-18T11:20:00",0.83333333333333437,0.4879825000000006,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта"," №3 25.03.2022"]
[4,"2022-04-13","ТП-270 - ТП-274","2022-04-13T09:47:00","2022-04-13T10:10:00",0.38333333339930187,2.790935000480297E-2,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта"," №4 26.04.2022"]
[5,"2022-04-20","ТП-543 яч.4 -- ТП-541 яч.2","2022-04-20T09:19:00","2022-04-20T09:55:00",0.60000000001552145,0.25717440000665287,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта"," №5 06.05.2022"]
[6,"2022-04-21","РП 28 яч.18 -- ТП 2317 яч.3","2022-04-21T20:20:00","2022-04-21T20:50:00",0.50000000007760814,2.1019500003262567E-2,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта"," №6 11.05.2022"]
[7,"2022-04-27","ТП-703 яч.4--ТП-704 яч.4","2022-04-27T16:08:00","2022-04-27T16:55:00",0.78333333330617094,0.37626163332028628,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта"," №7 12.05.2022"]
[8,"2022-05-16","КЛ -10кВ ТП-174 яч.2 -- ТП-179 яч.1","2022-05-16T00:36:00","2022-05-16T01:20:00",0.73333333329840866,0.10961279999477976,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта "," №9 23.05.2022"]
[9,"2022-05-19","тп-901 яч.4- тп-808 яч.3","2022-05-19T10:09:00","2022-05-19T10:58:00",0.81666666658517562,0.40626063329279466,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта "," №10 20.05.2022"]
[10,"2022-05-22","ТП-144-5 яч.2-- ТП-112-14 яч.6","2022-05-22T11:00:00","2022-05-22T11:45:00",0.74999999994179189,0.16885649998689489,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта","№11 24.05.2022"]
[11,"2022-05-09","ТП-230 яч.5-ТП-238 яч.2","2022-05-09T20:11:00","2022-05-09T20:50:00",0.65000000004268355,0.23924875001571072,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта"," №8 23.05.2022"]
[12,"2022-06-11","РП-13 яч.8 -- ТП-141 яч.3","2022-06-11T14:26:00","2022-06-11T14:55:00",0.48333333325960393,8.6585299986791972E-2,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта","№12 17.06.2022"]
[13,"2022-06-16","ТП-77 яч.6 - ТП-507 яч.4","2022-06-16T11:01:00","2022-06-16T12:15:00",1.2333333333954206,1.0155180333844556,"МУП \"Электросеть\", выход из строя  вследствие подвижек грунта ","№13 20.06.2022"]
[14,"2022-06-24","ТП-114 яч.3 -- ТП-115 яч.7","2022-06-24T23:18:00","2022-06-25T00:16:00",0.96666666667830825,8.344943333433831E-2,"МУП \"Электросеть\" резкие перепады температурного режима воздуха ,коррозия верхних слоев изоляции вызванная химическим составом грунта","№14 20.06.2022"]
[15,"2022-06-27","ТП-2510 яч.1 -- ТП-258 яч.4","2022-06-27T16:28:00","2022-06-27T17:02:00",0.56666666660069875,0.17310703331318125,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта","№15 04.06.2022"]
[16,"2022-07-04","ТП-144-5 яч.2-- ТП-112-14 яч.6","2022-07-04T10:58:00","2022-07-04T11:40:00",0.70000000005044649,6.9099100004979722E-2,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №16 07.07.2022"]
[17,"2022-07-18","РП-11 яч.18 -- ТП-2010 яч.6","2022-07-18T14:58:00","2022-07-18T15:20:00",0.36666666660069946,8.8717566650705432E-2,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №17 05.08.2022"]
[18,"2022-07-22","ТП-839 яч.3 -- ТП-833 яч.4","2022-07-22T07:54:00","2022-07-22T08:25:00",0.51666666658517535,6.1540683323626826E-2,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №18 08.08.2022"]
[19,"2022-07-31","ТП-110яч.3--ТП-97яч.2","2022-07-31T10:30:00","2022-07-31T10:57:00",0.44999999999999973,9.3186449999999935E-2,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №19 10.08.2022"]
[20,"2022-08-03","1 секция шин 10 кВ РП-26","2022-08-03T01:45:00","2022-08-03T02:36:00",0.85000000005820775,1.0545244500722135,"МУП \"Электросеть\" попадание крысы на шины в яч.11 РП-26 (повр. обор-ия нет, чистка опорных изоляторов)","№20 16.08.2022"]
[21,"2022-09-10","ТП-384 яч.5 -- ТП-387 яч.3","2022-09-10T08:07:00","2022-09-10T08:30:00",0.38333333341870501,0.19815420004413067,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №21 12.09.2022"]
[22,"2022-09-20","ТП-323 яч.1 --ТП-330 яч.1","13:42:00","2022-09-20",0.60069444444444442,263.91199999999998,"ООО \"Гоара-Строй\",  мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ ","№22  21.09.2022"]
[23,"2022-09-20","РП-21 яч.6 - ПС \"Зашекснинская\" яч.8                (каб. \"А\") ф. \"Котельная-1\"  ","14:42:00","2022-09-20",0.61249999999999993,0,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта","№23 20.09.2022"]
[24,"2022-10-08","ТП-105 яч.1--ТП-142 яч.1","2022-10-08T09:01:00","2022-10-08T10:01:00",0.99999999994567323,0.6959789999621897,"ИП Михай А. Г.,  мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ"," №24  26.10.2022"]
[25,"2022-10-09","КЛ-10кВ ТП-256, яч.3 - ТП-258, яч.6","2022-10-09T13:45:00","2022-10-09T14:58:00",1.2166666667248744,0.59861460002863898,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №25 14.10.2022"]
[26,"2022-10-11","РП-15 яч.5 - ТП 253 яч.4","2022-10-11T12:08:00","2022-10-11T12:10:00",3.3333333247961505E-2,9.1084666433384736E-3,"ООО \"Предприятие \"Агропромэнерго\",  мех.повреждение ковшом экскаватора, повреждение изоляции КЛ-10кВ"," №26 14.10.2022"]
[27,"2022-10-31","(ТП-508яч.2--ТП504яч.3)","2022-10-31T17:17:00","2022-10-31T18:00:00",0.71666666673263535,0.35260860003245736,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №27 10.11.2022"]
[28,"2022-11-16","ТП-1066 яч.1 - ТП-10611 яч.1","2022-11-16T04:25:00","2022-11-16T06:43:00",2.2999999999223899,0.12891959999564981,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №28 21.11.2022"]
[29,"2022-11-18","РП-13 яч.8 -- ТП-141 яч.3","2022-11-18T13:25:00","2022-11-18T13:49:00",0.39999999992238866,6.4096799987563402E-2,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №29 23.11.2022"]
[30,"2022-12-19","ТП-329 яч.1-ТП330 яч.5","2022-12-19T19:10:00","2022-12-19T19:53:00",0.71666666670547041,0.33215135001798429,"МУП \"Электросеть\",  коррозия верхних слоев изоляции вызванная химическим составом грунта"," №30 27.12.2022"]
[31,"2022-12-31","ПС\"Первомайская\" яч.204 - РП-24 яч.12","2022-12-31T09:27:00","2022-12-31T09:27:00",0,0,"МУП \"Электросеть\" ,  старение изоляции вследствие подвижек грунта"," №31 31.12.2022"]